## r2f_scenario_tracker
No | Scenario ID | Source | Root Cause | Final Stage | Chain Effect | Status
1 | healthy | RDA Baseline | Normal operation baseline. | N/A | Baseline performance at 80% and 58% load. | Received
2 | condenser_fouling | ASHRAE RP-1043 | Scale buildup on water tubes (SL1-SL4). | Performance Degradation | Reduced heat transfer efficiency; approach temperature widens. | Received
3 | evaporator_fouling | ASHRAE RP-1043 | Scale buildup on chilled water tubes (SL1-SL4). | Performance Degradation | Reduced cooling capacity; evaporator approach widens. | Received
4 | refrigerant_gas_leak | ASHRAE RP-1043 | Discharge-side gas leak (Slow/Moderate). | High Superheat Trip | Starvation of evaporator; loss of subcooling; eventual thermal trip. | Received
5 | refrigerant_liquid_leak | ASHRAE RP-1043 | High-side liquid line leak (Slow/Moderate). | High Superheat Trip | Rapid loss of charge; pressure collapse; protection trip. | Received
6 | reduced_condenser_water_flow | ASHRAE RP-1043 | Pump degradation or valve blockage. | High Condenser Pressure | Water flow falls, causing heat exchange to stall. Head pressure rises rapidly as the condenser can no longer reject heat. | Pending
7 | reduced_evaporator_water_flow | ASHRAE RP-1043 | CHW pump failure or strainer clog. | Low Evap Pressure / Freeze | Flow through the evaporator drops. The refrigerant over-cools the stagnant water, risking a freeze-up trip. | Pending
8 | refrigerant_overcharge | ASHRAE RP-1043 | Maintenance error (too much gas added). | High Condenser Pressure | Excess liquid stacks up in the condenser, reducing available surface area. Subcooling rises while head pressure climbs. | Pending
9 | noncondensable_gas | ASHRAE RP-1043 | Air/moisture leaked into the low side. | High Condenser Pressure | Air creates a blanket in the condenser that refrigerant cannot penetrate. This causes high head pressure similar to fouling, but persists after cleaning. | Pending
10 | excess_oil | ASHRAE RP-1043 | Oil migration from sump to tubes. | Capacity Loss | Oil coats the evaporator tubes, creating a thermal barrier. The machine loses cooling capacity even though the refrigerant charge is correct. | Pending
11 | expansion_valve_stuck_closed | OEM (Carrier/Trane/York/Daikin) | Expansion valve motor/linkage failure. | High Superheat Trip | The gate is closed. Refrigerant piles up in the condenser, starving the evaporator. Superheat spikes and the machine trips to protect the compressor. | Pending
12 | expansion_valve_stuck_open | OEM (Carrier/Trane/York/Daikin) | Expansion valve failure (full open). | Compressor Slugging | The gate is wide open. Liquid refrigerant floods the evaporator and enters the compressor suction, risking catastrophic slugging as liquid hits the spinning blades. | Pending
13 | igv_stuck_closed | OEM (Carrier/Trane/York/Daikin) | Inlet Guide Vane actuator failure. | Capacity Shortfall / Surge | The throttle is stuck at idle. The building gets hot because the chiller cannot ramp up, and the low flow puts the machine at risk of surging. | Pending
14 | cooling_tower_fan_failed | OEM (Carrier/Trane/York/Daikin) | Tower fan motor or belt failure. | High Entering CW Temp | Water returning from the tower gets hotter. This forces condenser pressure up until the compressor can no longer climb the pressure hill. | Pending
15 | low_oil_pressure | OEM (Carrier/Trane/York/Daikin) | Oil pump failure or plugged filter. | Low Oil Î”P Trip | The oil pump loses its pressure fight against the refrigerant. Without a differential pressure of 18–25 psid, the bearings lose their oil film and the machine trips to prevent damage. | Pending
16 | compressor_surge | OEM (Carrier/Trane/York/Daikin) | High Lift vs. Low Flow imbalance. | Surge Trip (Vibration) | Refrigerant gas loses momentum and falls backward through the impeller. This creates violent vibration shocks and power pulses until the machine trips. | Pending